## Main
Building [0] | Sensor ID [1] | Title [2] | Unit Label [3] | Sensor Group [4] | Sort Order [5] | Is Calc'd Field [6] | Calc or Transform Function [7] | Function Parameters [8]
Chugach View | chuvw_outdoor_temp | Site Outdoor Temp | deg F | Weather | 5
Chugach View | chuvw_boilers_fired | West Boilers Fired | units | Boiler | 10
Chugach View | chuvw_firing_rate | West Boiler Firing Rate | % | Boiler | 20
Chugach View | chuvw_firing_rate_tot | West Boiler Total Firing Rate | % | Boiler | 30
Chugach View | chuvw_gas_use | West Boiler Gas Use | Btu/hour | Boiler | 40 | TRUE | linear | id_val="chuvw_firing_rate_tot", slope=30000.0
Chugach View | chuvw_header_temp | West Header Temperature | deg F | Boiler | 50
Chugach View | chuvw_header_setpoint | West Header Setpoint | deg F | Boiler | 60
Chugach View | chuvw_boilers_online | West Boilers Online | units | Boiler | 70
Chugach View | chuvw_boiler1_status | West Boiler 1 Status | code | Boiler | 80
Chugach View | chuvw_boiler2_status | West Boiler 2 Status | code | Boiler | 90
Chugach View | chuvw_lead_boiler | West Lead Boiler | ID | Boiler | 100
Chugach View | chuvw_io_status | West Boiler I/O Status | code | Boiler | 110
Chugach View | chuvw_fault_code | West Boiler Fault Code | code | Boiler | 120

## 2014-07-15
Building [0] | Sensor ID [1] | Title [2] | Unit Label [3] | Sensor Group [4] | Sort Order [5] | Is Calc'd Field [6] | Calc or Transform Function [7] | Function Parameters [8]
Chugach View | anc_merril_temp |  |  | Weather | 10
Chugach View | anc_merril_wind |  |  | Weather | 20
Chugach View | 53805 | Electric Meter | kW | Utilities/Fuel | 10 |  | rate*0.096*3600.0
Chugach View | 53802 | Gas Meter West | Btu/hour | Utilities/Fuel | 20 |  | rate*1010.0*3600.0 | max_rate=1.5
Chugach View | 53804 | Gas Meter East | Btu/hour | Utilities/Fuel | 30 |  | rate*1010.0*3600.0 | max_rate=1.5
Chugach View | chuvw_gas_total | Gas Meter Total | Btu/hour | Utilities/Fuel | 40 | TRUE | AplusBplusCplusD | id_A_sync="53802", id_B="53804"
Chugach View | 55439 | DHW to Bldg Temp | deg F | Domestic Hot Water | 10
Chugach View | 55436 | DHW Tank Temp | deg F | Domestic Hot Water | 20
Chugach View | 55437 | DHW Recirc Return Temp | deg F | Domestic Hot Water | 30
Chugach View | 55442 | DHW Circ Pump On/Off | 1=On 0=Off | Domestic Hot Water | 40
Chugach View | chuvw_dhw_circ_run | DHW Circ Pump Runtime | Runtime Fraction | Domestic Hot Water | 50 | TRUE | runtimeFromOnOff | onOffID="55442"
Chugach View | 55446 | 1st Floor Hall Occup State | 1=Occupied 0=Vacant | Space Conditions, Occupancy | 10
Chugach View | chuvw_occup_run_1 | 1st Floor Hall Occup Fraction | Occupied Fraction | Space Conditions, Occupancy | 20 | TRUE | runtimeFromOnOff | onOffID="55446"
Chugach View | 55445 | 2nd Floor Hall Occup State | 1=Occupied 0=Vacant | Space Conditions, Occupancy | 30
Chugach View | chuvw_occup_run_2 | 2nd Floor Hall Occup Fraction | Occupied Fraction | Space Conditions, Occupancy | 40 | TRUE | runtimeFromOnOff | onOffID="55445"
Chugach View | 55444 | Snowmelt Circ Pump On/Off | 1=On 0=Off | Snowmelt | 10
Chugach View | chuvw_snow_circ_run | Snowmelt Circ Pump Runtime | Runtime Fraction | Snowmelt | 20 | TRUE | runtimeFromOnOff | onOffID="55444"
Chugach View | 55438 | Snowmelt to Slab Temp | deg F | Snowmelt | 30
Chugach View | 55440 | Snowmelt from Slab Temp | deg F | Snowmelt | 40

## 2014-07-08
Building [0] | Sensor ID [1] | Title [2] | Unit Label [3] | Sensor Group [4] | Sort Order [5] | Calc Function [6] | Function Parameters [7]
511 Oklahoma St | Okla511_outdoor_temp | Site Outdoor Temp | deg F | Weather | 10
511 Oklahoma St | elmendorf_temp | Elmendorf Temp | deg F | Weather | 20 | getInternetTemp | stnCode="PAED"
511 Oklahoma St | elmendorf_wind | Elmendorf Wind Speed | mph | Weather | 30 | getInternetWindSpeed | stnCode="PAED"
511 Oklahoma St | Okla511_firing_rate | Boiler Firing Rate | % | Boiler | 10
511 Oklahoma St | Okla511_outlet_temp | Boiler Outlet Temp | deg F | Boiler | 20
511 Oklahoma St | Okla511_inlet_temp | Boiler Inlet Temp | deg F | Boiler | 30
511 Oklahoma St | Okla511_stack_temp | Stack Temp | deg F | Boiler | 40
511 Oklahoma St | Okla511_demand_source | Source of Demand | code | Boiler | 50
511 Oklahoma St | Okla511_ch_demand | Space Heat Demand | 1=On 0=Off | Boiler | 60
511 Oklahoma St | Okla511_dhw_demand | DHW Demand | 1=On 0=Off | Boiler | 70
511 Oklahoma St | Okla511_lockout_code | Boiler Lockout Code | code | Boiler, Alarms | 10
511 Oklahoma St | Okla511_alarm_reason | Boiler Alarm Reason | code | Boiler, Alarms | 20
511 Oklahoma St | Okla511_alarm_code | Boiler Alarm Code | code | Boiler, Alarms | 30
511 Oklahoma St | Okla511_limits | Boiler Limits Reached | code | Boiler, Alarms | 40
511 Oklahoma St | Okla511_flame_signal | Boiler Flame Signal | Volts | Boiler, Alarms | 50
511 Oklahoma St | Okla511_ch_setpoint | Boiler Heating Setpoint | deg F | Boiler, Setpoints | 10
511 Oklahoma St | Okla511_dhw_setpoint | Boiler DHW Setpoint | deg F | Boiler, Setpoints | 20
511 Oklahoma St | Okla511_active_setpoint | Boiler Active Setpoint | deg F | Boiler, Setpoints | 30
511 Oklahoma St | Okla511_uptime | Monitoring System Uptime | seconds | Miscellaneous | 10
511 Oklahoma St | 28.71F34C050000 | DHW to Building Temp | deg F | Domestic Hot Water | 10
511 Oklahoma St | 28.B4974C050000 | DHW Tank Temp | deg F | Domestic Hot Water | 20
511 Oklahoma St | 12.1EEAA0000000 | DHW Circ Pump State | 1=On 0=Off | Domestic Hot Water | 30
511 Oklahoma St | Okla511_dhw_circ_run | DHW Circ Pump Runtime | Runtime Fraction | Domestic Hot Water | 40 | runtimeFromOnOff | onOffID="12.1EEAA0000000"
511 Oklahoma St | 28.F97D4C050000 | Zone #1 Supply Temp | deg F | Space Heating | 10
511 Oklahoma St | 28.EAEB4C050000 | Zone #2 Supply Temp | deg F | Space Heating | 20
511 Oklahoma St | 28.32784C050000 | Zone #3 Down Supply Temp | deg F | Space Heating | 30
511 Oklahoma St | 28.F8134C050000 | Zone #3 Up Supply Temp | deg F | Space Heating | 40
511 Oklahoma St | 28.21D44C050000 | Boiler Room Temp | deg F | Space Conditions, Temperature | 10
158 Burton St | Burt158_outdoor_temp | Site Outdoor Temp | deg F | Weather | 10
158 Burton St | elmendorf_temp |  |  | Weather | 20
158 Burton St | elmendorf_wind |  |  | Weather | 30
158 Burton St | Burt158_firing_rate | Boiler Firing Rate | % | Boiler | 10
158 Burton St | Burt158_outlet_temp | Boiler Outlet Temp | deg F | Boiler | 20
158 Burton St | Burt158_inlet_temp | Boiler Inlet Temp | deg F | Boiler | 30
158 Burton St | Burt158_stack_temp | Stack Temp | deg F | Boiler | 40
158 Burton St | Burt158_demand_source | Source of Demand | code | Boiler | 50
158 Burton St | Burt158_ch_demand | Space Heat Demand | 1=On 0=Off | Boiler | 60
158 Burton St | Burt158_dhw_demand | DHW Demand | 1=On 0=Off | Boiler | 70
158 Burton St | Burt158_lockout_code | Boiler Lockout Code | code | Boiler, Alarms | 10
158 Burton St | Burt158_alarm_reason | Boiler Alarm Reason | code | Boiler, Alarms | 20
158 Burton St | Burt158_alarm_code | Boiler Alarm Code | code | Boiler, Alarms | 30
158 Burton St | Burt158_limits | Boiler Limits Reached | code | Boiler, Alarms | 40
158 Burton St | Burt158_flame_signal | Boiler Flame Signal | Volts | Boiler, Alarms | 50
158 Burton St | Burt158_ch_setpoint | Boiler Heating Setpoint | deg F | Boiler, Setpoints | 10
158 Burton St | Burt158_dhw_setpoint | Boiler DHW Setpoint | deg F | Boiler, Setpoints | 20
158 Burton St | Burt158_active_setpoint | Boiler Active Setpoint | deg F | Boiler, Setpoints | 30
158 Burton St | Burt158_uptime | Monitoring System Uptime | seconds | Miscellaneous | 10
158 Burton St | 28.88624D050000 | DHW to Building Temp | deg F | Domestic Hot Water | 10
158 Burton St | 28.2A794D050000 | DHW Tank Temp | deg F | Domestic Hot Water | 20
158 Burton St | 12.??? | DHW Circ Pump State | 1=On 0=Off | Domestic Hot Water | 30
158 Burton St | Burt158_dhw_circ_run | DHW Circ Pump Runtime | Runtime Fraction | Domestic Hot Water | 40 | runtimeFromOnOff | onOffID="12.???"
158 Burton St | 28.5DB24C050000 | Zone #1 Supply Temp | deg F | Space Heating | 10
158 Burton St | 28.51304C050000 | Zone #2 Supply Temp | deg F | Space Heating | 20
158 Burton St | 28.D52C4C050000 | Zone #3 Supply Temp | deg F | Space Heating | 30
158 Burton St | 28.4E834C050000 | Zone #4 Supply Temp | deg F | Space Heating | 40
158 Burton St | 28.DBB44D050000 | Garage Zone Return Temp | deg F | Space Heating | 50
158 Burton St | 28.EFED4C050000 | Boiler Room Temp | deg F | Space Conditions, Temperature | 10
4319 Reka Dr | 28.7CCD4B050000 | DHW to Building Temp | deg F | Domestic Hot Water | 10
4319 Reka Dr | 28.C2BE4D050000 | DHW Tank Temp | deg F | Domestic Hot Water | 20
4319 Reka Dr | 12.0DF5A0000000 | DHW Circ Pump State | 1=On 0=Off | Domestic Hot Water | 30
4319 Reka Dr | Reka_dhw_circ_run | DHW Circ Pump Runtime | Runtime Fraction | Domestic Hot Water | 40 | runtimeFromOnOff | onOffID="12.0DF5A0000000"
1142 Ptar Park | 28.226A4D050000 | Boiler Supply Temp | deg F | Boiler | 10
1142 Ptar Park | 28.6D794D050000 | Boiler Mixed Return Temp | deg F | Boiler | 20
1142 Ptar Park | 12.B1517D000000 | Boiler Injection Pump State | 1=On 0=Off | Boiler | 30
1142 Ptar Park | Ptar1142_boiler_circ_run | Boiler Injection Pump Runtime | Runtime Fraction | Boiler | 40 | runtimeFromOnOff | onOffID="12.B1517D000000"
1142 Ptar Park | 28.6D7F4C050000 | DHW to Building Temp | deg F | Domestic Hot Water | 10
1142 Ptar Park | 28.98844D050000 | DHW Short Tank Temp | deg F | Domestic Hot Water | 20
1142 Ptar Park | 28.7FB74D050000 | DHW Tall Tank Temp | deg F | Domestic Hot Water | 30
1142 Ptar Park | 28.9C9B4C050000 | DHW Recirc Return Temp | deg F | Domestic Hot Water | 40
1142 Ptar Park | 28.ADEA4C050000 | DHW Return to Boiler Temp | deg F | Domestic Hot Water | 50
1142 Ptar Park | 12.FDF4A0000000 | DHW Short Circ Pump State | 1=On 0=Off | Domestic Hot Water | 60
1142 Ptar Park | Ptar1142_dhw_short_run | DHW Short Circ Pump Runtime | Runtime Fraction | Domestic Hot Water | 70 | runtimeFromOnOff | onOffID="12.FDF4A0000000"
1142 Ptar Park | 12.96347D000000 | DHW Tall Circ Pump State | 1=On 0=Off | Domestic Hot Water | 80
1142 Ptar Park | Ptar1142_dhw_tall_run | DHW Tall Circ Pump Runtime | Runtime Fraction | Domestic Hot Water | 90 | runtimeFromOnOff | onOffID="12.96347D000000"
1142 Ptar Park | 28.69764D050000 | Building Return Temp | deg F | Space Heating | 10